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NUTFIELD CHURCH (C OF E) PRIMARY SCHOOL

HEALTH AND SAFETY AND PREMISES MANAGEMENT OVERVIEW 2025-26
MONITORING VISIT On 11th February 2026

1. ACTIONS SINCE THE PREVIOUS MEETING HELD ON THURSDAY 16TH MAY 2024:
	SAFEGUARDING

	08/10/2025
	CFG raised a safeguarding concern around the condition of the perimeter fence.  Upon inspection the fence has been badly damaged by both intruders and wildlife over its lifespan and also suffers from areas of dilapidation. The Fence to the North has gaps allowing access to Kentwyns Wood.  To the East the fence supports are crumbling and the chain-link badly damaged in places. To the south, there is no boundary fence in place and the hedge which bounds the allotments has many gaps.  There have been intruders to the site (at night) and children have left the grounds.  JC meeting with Diocesan representatives on   Thur 4th December



	STATUTORY CHECKS / INSPECTIONS

	Fire
	
	Unplanned fire drills.
No Unplanned Fire Drills since 24/06/2025. 

Planned Fire Drill 
9th December 2025 – Whole School

	
	24/07/2025
	RJ Fire – Completed service and inspection of fire alarm, inspection of firefighting equipment, and annual discharge test and inspection of emergency lighting.  Batteries were required for many of the sensors.  These are stored on site. 
None of the fire extinguishers required replacement.   
Firefighting equipment report
Fire alarm system and emergency lighting report

	Trees
	09/08/2025
	The SCC 3 yearly tree inspection was completed and there were numerous recommendations which required the felling of two trees which were deemed to be dangerous and the significant reduction in the canopies of 3 other trees.  The Work was carried out in August.
Tree Condition Assessment

	Boiler and Associated Controls
	
	Boiler Service not carried out due to new Gas installation works ongoing.  

	
	
	All Boiler controls and hot water related works and statutory checks are currently suspended due to ongoing boiler replacement. 

	Intruder Alarm
	23/07/2025


30/07/2025
	Admiral Security – Onsite to complete the bi-annual service of the intruder alarm system.

Intruder alarm callout following planned School powerdown

Alarm Maintenance Certificate
Intruder Alarm Callout


	Dining Tables
	27/07/2025
	The 10 x new folding dining tables need to be serviced each year. We have entered a three-year Preventive Maintenance Agreement with the manufacturer, SICO Europe Ltd. This was their first service.
SICO Engineers Job Sheet

	Asbestos
	01/07/2025
	A refurbishment survey was carried out ahead of electrical works to the main incoming electrical distribution panel.  The panel contains Asbestos Carriers which upon decommission will need to be disposed of in accordance with the regulations.  Awaiting 

	
	26/09/2025
	Tetra Tech – Onsite to complete the Asbestos Re-Inspection of Risk Assessment. 
Asbestos re-inspection survey report

	Legionella
	24/07/2024
	Legionella re-Inspection not due until 2026 however ongoing temperature checks are carried out weekly and recorded by the premises manager.



	BUILDING PREMISES WORKS (EXTERNAL CONTRACTORS)

	
	
	

	Doors
	20/08/2025
	Orbital construction replaced 3x doorframes to the hall which were rotten and had fallen away giving rise to door dropping issues

	
	
	

	Cleaning
	27/07/2025
	Solo Service Group (contract cleaners) deep clean during the Summer holidays.


	
	11/08/25-
12/08/25
	ASF – Onsite to deep clean all carpets, clean windows inside and out, clean roof lights, skylights and upper school outdoor covered area. This year, they also cleaned the green metal structure of the KS2 canopy and all outside UPVC frames and ledges.

	
	
	

	Electrical
	29/05/2025


27/08/2025
	JTD Electrical  - Installation of emergency light fitting and key switch in boiler room. (H&S)

JTD Electrical – Installation of additional wall sockets following review of use of extension cables. (H&S)
(Invoices)



	UNPLANNED EVENTS

	Japanese knotweed
	24/06/2024
	Japanese Knotweed is present at the northern perimeter fence of the property.  There is a large infestation around 70sqm in Kentwyns wood which is the likely cause of the infestation.  JC tried to contact the landowner (Mr Broadbent) without success.  JC has contacted the District council and investigations are ongoing

	Fire Alarm
	NA
	No Unplanned Events
One Planned Fire Drill carried out on 28/01/2026

	Intruder Alarm
	NA
	No unplanned Events

	
	
	



	CPD

	DATE
	TRAINING

	02/10/2025
	Staff completed their schools first aid training run by Event medical Team Ltd

	15/10/2025
	Ark staff (Offer, Koncius, Harrison, Cordey & Wahab) completed their Basic Food Hygene training via online training Ltd



	OTHER

	VA-SCA Plant Room Works / ASHP
	At 02/12/2025
	ASHP installed but not operational due to electrical loading issue with UKPN.  
Boiler works and controls not yet signed off.  Dispute between SJP Mechanical and Carrier yet to be resolved. 

	
	
	ASHP switched off and drained down during cold snap to prevent expansion damage to installation

	
	
	

	Policy & Compliance

	Various
	01/10/2025
	Display Energy Certificate now issued (Finally)

	
	15/12/2025
	Annual Commercial Catering Inspection carried out without further remedials 



	Upcoming Works

	Lighting
	Quotes received – planning permission required.  Some challenges exist trying to identify the legal owner of the premises.  (See quote)

	Flooring 
	Quote received to replace the lino and the carpet in KS2 all classrooms.  Intention to complete the works either at Easter or the Summer break(See quote)

	15/10/2025
	Upcoming Works up to date (See Premises & H&S tracker)
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