Service inspection certificate: 
fire alarm & emergency lighting

RJ Fire
Fire & Security Specialists
32 Cinnabar Drive
Sittingbourne
Kent ME10 5LA




CLIENT
FINANCE OFFICE
NUTFIELD C/E SCHOOL
59 MID STREET
SOUTH NUTFIELD
RH1 4JJ
CERTIFICATE N0:3752
WORKS REF N0:

INSPECTION DATE:
SERVICE iNSPECTIONS AT:
sERVICE inspections:
Next Service:
24/07/2025
NUTFIELD SCHOOL SOUTH NUTFIELD RH1 4JJ
BI ANNUAL
JANUARY 2026 

DISCIPLINES:
service & maintenance carried out:


FIRE  ALARM: e/LIGHTING

PASS
FAIL
SYSTEM TESTS

YES

CONTROL PANEL
Operational (EDA ZERIO PLUS RADIO SYSTEM)
YES

SMOKE DETECTORS
Operational (EDA OPTICAL DETECTORS)
YES
LOW BATTERY FAULTS
HEAT DETECTORS
Operational (EDA RATE OF RISE DETECTORS)
YES

CALL POINTS
Operational (EDA)
YES
LOW BATTERY FAULTS
BELLS/SOUNDERS
Operational (ZERIO COMBINED BASE SOUNDERS)
YES

EMERGENCY LIGHTING
3 HOUR ANNUAL DISCHARGE TEST
YES
X8 FAILURES
BEACONS
Operational
YES

RELAYS
N/A


INTERLINKS
N/A


BEAMS
N/A


DIALLER
N/A


ROLLER SHUTTER
Operational


ZONE CHART

YES

BATTERIES
Operational (PANEL SHOWS MULTIPLE FAULTS, DEVICE BATTERY REPLACEMENTS REQUIRED)
YES

LOG BOOK SIGNED 
                                                                               


SERVICE COMPLETE

YES

SERVICE ENGINEER:

R.Jones

X16 BATTERY FAULTS ON VARIOUS DEVICES AROUND SITE:X16 BATTERY PACKS REQUIRED.
X6 600X600 EMERGENCY LIGHTS FAILED 
X2 CIRCULAR ENERGENCY LIGHTS FAILED




















