| # Service inspection certificate: # fire alarm & emergency lighting |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| RJ Fire Fire & Security Specialists 32 Cinnabar Drive Sittingbourne Kent ME10 5LA |  |  |  |  |  |  | CLIENT FINANCE OFFICE NUTFIELD C/E SCHOOL 59 MID STREET SOUTH NUTFIELD RH1 4JJ |  |
| CERTIFICATE N0:3888 |  |  |  |  |  |  |  |  |
| WORKS REF N0: |  |  |  |  |  |  |  |  |
| INSPECTION DATE: | SERVICE iNSPECTIONS AT: |  |  |  | sERVICE inspections: |  |  | Next Service: |
| 15/01/2026 | NUTFIELD SCHOOL SOUTH NUTFIELD RH1 4JJ |  |  |  | BI ANNUAL |  |  | JULY 2026 |
| DISCIPLINES: | service & maintenance carried out: |  |  |  |  |  |  |  |
| FIRE ALARM: e/LIGHTING |  |  |  |  | PASS |  |  | FAIL |
| SYSTEM TESTS |  |  |  |  | YES |  |  |  |
| CONTROL PANEL | Operational (EDA ZERIO PLUS RADIO SYSTEM) |  |  |  | YES |  |  |  |
| SMOKE DETECTORS | Operational (EDA OPTICAL DETECTORS) |  |  |  | YES |  |  |  |
| HEAT DETECTORS | Operational (EDA RATE OF RISE DETECTORS) |  |  |  | YES |  |  |  |
| CALL POINTS | Operational (EDA) |  |  |  | YES |  |  |  |
| BELLS/SOUNDERS | Operational (ZERIO COMBINED BASE SOUNDERS) |  |  |  | YES |  |  |  |
| EMERGENCY LIGHTING | 3 HOUR DISCHARGE TEST DUE JULY 2026 |  |  |  |  |  |  |  |
| BEACONS | Operational |  |  |  | YES |  |  |  |
| RELAYS | N/A |  |  |  |  |  |  |  |
| INTERLINKS | N/A |  |  |  |  |  |  |  |
| BEAMS | N/A |  |  |  |  |  |  |  |
| DIALLER | N/A |  |  |  |  |  |  |  |
| REMEDIAL WORKS |  |  |  |  |  |  |  |  |
| ZONE CHART |  |  |  |  | YES |  |  |  |
| BATTERIES | Operational |  |  |  | YES |  |  |  |
| LOG BOOK SIGNED |  |  |  |  |  |  |  |  |
| SERVICE COMPLETE |  |  |  |  | YES |  |  |  |
| SERVICE ENGINEER: |  |  |  |  |  |  |  | R.Jones |
| . |  |  |  |  |  |  |  |  |